## Delta Wye-Delta Delta 3 Phase
[5 empty] | Single | 5 | 45 |  | 2400 | 120 | Delta Delta Voltages Bayonet Fuse Chart | [17 empty] | Delta Wye Voltages Bayonet Fuse Chart | [17 empty] | Wye Delta Voltage Bayonet Fuse Chart | [17 empty] | Wye Wye Voltage Bayonet Fuse Chart
[5 empty] | Three | 10 | 75 |  | 4160 | 208 | HIGH AMP | DUAL SENSING |  |  | * CURRENT SENSING |  |  |  |  | 3 Phase Transformer (Phase to Phase) Applications | [8 empty] | DUAL SENSING |  |  | * CURRENT SENSING |  |  |  |  | 3 Phase Transformer (Phase to Phase) Applications | [8 empty] | DUAL SENSING |  |  | CURRENT SENSING |  |  |  | 3 Phase Transformer (Phase to Phase) Applications | [9 empty] | DUAL SENSING |  |  | CURRENT SENSING |  |  |  | 3 Phase Transformer (Phase to Phase) Applications
[6 empty] | 15 | 112.5 |  | 4800 | 240 |  | 8.3 KV | [5 empty] | 15.5 / 17.2 KV | [7 empty] | 23 KV |  |  | 8.3 KV | [5 empty] | 15.5 / 17.2 KV | [7 empty] | 23 KV |  |  | 8.3 KV | [5 empty] | 15.5 / 17.2 KV | [7 empty] | 23 KV |  |  | 8.3 KV | [5 empty] | 15.5 / 17.2 KV | [7 empty] | 23 KV
Bayonet Fusing Generator | [5 empty] | 25 | 150 |  | 7200 | 480 | Kva | 2400DD | 4160DD | 4800DD | 7200DD | 7620DD | 8320DD | 12000DD | 12470DD | 13200DD | 13800DD | 14400DD | 20800DD | 22900DD | 24940DD | 23000DD | 27600DD | 34500DD | 2400DY | 4160DY | 4800DY | 7200DY | 7620DY | 8320DY | 12000DY | 12470DY | 13200DY | 13800DY | 14400DY | 20800DY | 22900DY | 24940DY | 23000DY | 27600DY | 34500DY | 2400YD | 4160YD | 4800YD | 7200YD | 7620YD | 8320YD | 12000YD | 12470YD | 13200YD | 13800YD | 14400YD | 20800YD | 22900YD | 24940YD | 23000YD | 27600YD | 34500YD | 2400YY | 4160YY | 4800YY | 7200YY | 7620YY | 8320YY | 12000YY | 12470YY | 13200YY | 13800YY | 14400YY | 20800YY | 22900YY | 24940YY | 23000YY | 27600YY | 34500YY
[6 empty] | 37.5 | 225 |  | 7620 | 575 | 45 | C10 | C08 | C08 | C05 | C05 | C05 | C03 | C03 | C03 | C03 | C03 | N/A | N/A | N/A | N/A | N/A | N/A | C10 | C08 | C08 | C05 | C05 | C05 | C03 | C03 | C03 | C03 | C03 | N/A | N/A | N/A | N/A | N/A | N/A | C10 | C08 | C08 | C05 | C05 | C05 | C03 | C03 | C03 | C03 | C03 | N/A | N/A | N/A | N/A | N/A | N/A | C10 | C08 | C08 | C05 | C05 | C05 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | N/A | N/A | N/A
|  |  | DELTA / WYE CONFIGURATION |  |  | 50 | 300 |  | 8320 | 600 | 75 | C12 | C10 | C10 | C08 | C08 | C08 | C05 | C05 | C05 | C05 | C05 | N/A | N/A | N/A | N/A | N/A | N/A | C12 | C10 | C10 | C08 | C08 | C08 | C05 | C05 | C05 | C05 | C05 | N/A | N/A | N/A | N/A | N/A | N/A | C12 | C10 | C10 | C08 | C08 | C08 | C05 | C05 | C05 | C05 | C05 | N/A | N/A | N/A | N/A | N/A | N/A | C12 | C10 | C10 | C08 | C08 | C08 | C05 | C05 | C05 | C05 | C05 | C03 | C03 | C03 | N/A | N/A | N/A
Phase |  | select |  |  |  | 75 | 500 |  | 12000 | 2400 | 112.5 | C14 | C12 | C10 | C08 | C08 | C08 | C08 | C08 | C08 | C08 | C08 | N/A | N/A | N/A | N/A | N/A | N/A | C14 | C12 | C10 | C08 | C08 | C08 | C08 | C08 | C08 | C08 | C08 | N/A | N/A | N/A | N/A | N/A | N/A | C14 | C12 | C10 | C08 | C08 | C08 | C08 | C08 | C08 | C08 | C08 | N/A | N/A | N/A | N/A | N/A | N/A | C14 | C12 | C10 | C08 | C08 | C08 | C08 | C08 | C08 | C08 | C08 | C05 | C05 | C05 | N/A | N/A | N/A
KVA |  | select |  |  |  | 100 | 750 |  | 12470 | 4160 | 150 | C14 | C12 | C12 | C10 | C10 | C10 | C08 | C08 | C08 | C08 | C08 | N/A | N/A | N/A | N/A | N/A | N/A | C14 | C12 | C12 | C10 | C10 | C10 | C08 | C08 | C08 | C08 | C08 | N/A | N/A | N/A | N/A | N/A | N/A | C14 | C12 | C12 | C10 | C10 | C10 | C08 | C08 | C08 | C08 | C08 | N/A | N/A | N/A | N/A | N/A | N/A | C14 | C12 | C12 | C10 | C10 | C10 | C08 | C08 | C08 | C08 | C08 | C05 | C05 | C05 | N/A | N/A | N/A
HV |  | select | select |  |  | 167 | 1000 |  | 13200 | 4800 | 225 | C18 | C14 | C14 | C12 | C12 | C12 | C10 | C10 | C10 | C10 | C10 | N/A | N/A | N/A | N/A | N/A | N/A | C18 | C14 | C14 | C12 | C12 | C12 | C10 | C10 | C10 | C10 | C10 | N/A | N/A | N/A | N/A | N/A | N/A | C18 | C14 | C14 | C12 | C12 | C12 | C10 | C10 | C10 | C10 | C10 | N/A | N/A | N/A | N/A | N/A | N/A | C18 | C14 | C14 | C12 | C12 | C12 | C10 | C10 | C10 | C10 | C10 | C08 | C08 | C08 | N/A | N/A | N/A
LV |  | select | select |  |  | 250 | 1500 |  | 13800 | 6900 | 300 | C18 | C14 | C14 | C12 | C12 | C12 | C10 | C10 | C10 | C10 | C10 | N/A | N/A | N/A | N/A | N/A | N/A | C18 | C14 | C14 | C12 | C12 | C12 | C10 | C10 | C10 | C10 | C10 | N/A | N/A | N/A | N/A | N/A | N/A | C18 | C14 | C14 | C12 | C12 | C12 | C10 | C10 | C10 | C10 | C10 | N/A | N/A | N/A | N/A | N/A | N/A | C18 | C14 | C14 | C12 | C12 | C12 | C10 | C10 | C10 | C10 | C10 | C08 | C08 | C08 | N/A | N/A | N/A
[6 empty] | 333 | 2000 |  | 14400 | 7200 | 500 | C05CB | C18 | C18 | C14 | C14 | C14 | C12 | C12 | C12 | C12 | C12 | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C18 | C18 | C14 | C14 | C14 | C12 | C12 | C12 | C12 | C12 | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C18 | C18 | C14 | C14 | C14 | C12 | C12 | C12 | C12 | C12 | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C18 | C18 | C14 | C14 | C14 | C12 | C12 | C12 | C12 | C12 | C10 | C10 | C10 | N/A | N/A | N/A
| QTY | TYPE | SIZE | AMPS |  | 500 | 2500 |  | 20800 | 8320 | 750 | N/A | C18 | C18 | C18 | C18 | C18 | C14 | C14 | C14 | C14 | C14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C18 | C18 | C18 | C18 | C18 | C14 | C14 | C14 | C14 | C14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C18 | C18 | C18 | C18 | C18 | C14 | C14 | C14 | C14 | C14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C18 | C18 | C18 | C18 | C18 | C14 | C14 | C14 | C14 | C14 | C12 | C12 | C12 | N/A | N/A | N/A
YOUR FUSING |  |  | FALSE |  |  |  | 3000 |  | 22900 | 12470 | 1000 | N/A | N/A | C05CB | C18 | C18 | C18 | C14 | C14 | C14 | C14 | C14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C18 | C18 | C18 | C14 | C14 | C14 | C14 | C14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C18 | C18 | C18 | C14 | C14 | C14 | C14 | C14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C18 | C18 | C18 | C14 | C14 | C14 | C14 | C14 | C12 | C12 | C12 | N/A | N/A | N/A
[7 empty] | 3750 |  | 23000 |  | 1500 | N/A | N/A | N/A | C05CB | C05CB | C05CB | C17 | C17 | C17 | C16 | C16 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C05CB | C05CB | C17 | C17 | C17 | C16 | C16 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C05CB | C05CB | C18 | C18 | C18 | C18 | C18 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C05CB | C05CB | C18 | C18 | C18 | C18 | C18 | C14 | C14 | C14 | N/A | N/A | N/A
[9 empty] | 24940 |  | 2000 | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C05CB | C17 | C17 | C17 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C05CB | C17 | C17 | C17 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C05CB | C17 | C17 | C17 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C05CB | C17 | C17 | C17 | C16 | C16 | C16 | N/A | N/A | N/A
[9 empty] | 27600 |  | 2500 | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C05CB | C05CB | C05CB | C05CB | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C05CB | C05CB | C05CB | C05CB | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C05CB | C05CB | C05CB | C05CB | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | C05CB | C05CB | C05CB | C05CB | C05CB | C17 | C17 | C17 | N/A | N/A | N/A
[9 empty] | 34500 |  | 3000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[11 empty] | 3750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[11 empty] | ( * ) | Indicates Current Sensing Fuses | [16 empty] | ( * ) | Indicates Current Sensing Fuses | [16 empty] | ( * ) | Indicates Current Sensing Fuses | [16 empty] | ( * ) | Indicates Current Sensing Fuses
[5 empty] | KVA | HV | LV | HV CONFIG | LV CONFIG
[5 empty] | select | select | select |  |  |  |  | Dual Sensing Fuses | [5 empty] | Current Sensing Fuses | [11 empty] | Dual Sensing Fuses | [5 empty] | Current Sensing Fuses | [11 empty] | Dual Sensing Fuses | [5 empty] | Current Sensing Fuses | [11 empty] | Dual Sensing Fuses | [6 empty] | Current Sensing Fuses
[5 empty] | 1P UID | select | [7 empty] | Fuse | Isolation | Isolatoin |  |  |  | Fuse | Isolation | Isolatoin | [9 empty] | Fuse | Isolation | Isolatoin |  |  |  | Fuse | Isolation | Isolatoin | [9 empty] | Fuse | Isolation | Isolatoin |  |  |  | Fuse | Isolation | Isolatoin | [9 empty] | Fuse | Isolation | Isolatoin |  |  |  |  | Fuse | Isolation | Isolatoin
[5 empty] | 3P UID | select | Return 3/1 | #N/A | #N/A |  |  | Fuse Size | Amps | Co. # | Link | Link Co. # |  | Fuse Size | Amps | Co. # | Link | Link Co. # | [7 empty] | Fuse Size | Amps | Co. # | Link | Link Co. # |  | Fuse Size | Amps | Co. # | Link | Link Co. # | [7 empty] | Fuse Size | Amps | Co. # | Link | Link Co. # |  | Fuse Size | Amps | Co. # | Link | Link Co. # | [7 empty] | Fuse Size | Amps | Co. # | Link | Link Co. # |  |  | Fuse Size | Amps | Co. # | Link | Link Co. #
[5 empty] | selectselect | [6 empty] | C03 | 3 | 00130 | A01 | 00120 |  | C16 | 100 | 00144 | A05 | 00123 | [7 empty] | C03 | 3 | 00130 | A01 | 00120 |  | C16 | 100 | 00144 | A05 | 00123 | [7 empty] | C03 | 3 | 00130 | A01 | 00120 |  | C16 | 100 | 00144 | A05 | 00123 | [7 empty] | C03 | 3 | 00130 | A01 | 00120 | Dual Sensing Fuses |  | C16 | 100 | 00144 | A05 | 00123
[5 empty] | SingleDelta | 2 | [5 empty] | C05 | 8 | 00131 | A02 | 00121 |  | C17 | 140 | 00137 | A05 | 00123 | [7 empty] | C05 | 8 | 00131 | A02 | 00121 |  | C17 | 140 | 00137 | A05 | 00123 | [7 empty] | C05 | 8 | 00131 | A02 | 00121 |  | C17 | 140 | 00137 | A05 | 00123 | [7 empty] | C05 | 8 | 00131 | A02 | 00121 | Dual Sensing Fuses |  | C17 | 140 | 00137 | A05 | 00123
[5 empty] | SingleWye | 1 | [5 empty] | C08 | 15 | 00132 | A03 | 00122 | [13 empty] | C08 | 15 | 00132 | A03 | 00122 | [13 empty] | C08 | 15 | 00132 | A03 | 00122 | [13 empty] | C08 | 15 | 00132 | A03 | 00122 | Dual Sensing Fuses
[5 empty] | ThreeDelta | 3 | [5 empty] | C10 | 25 | 00133 | A05 | 00123 |  | High Amp Fuses | [11 empty] | C10 | 25 | 00133 | A05 | 00123 |  | High Amp Fuses | [11 empty] | C10 | 25 | 00133 | A05 | 00123 |  | High Amp Fuses | [11 empty] | C10 | 25 | 00133 | A05 | 00123 | Dual Sensing Fuses |  | High Amp Fuses
[5 empty] | ThreeWye | 3 | [5 empty] | C12 | 50 | 00134 | A06 | 00124 |  |  |  | Fuse | Isolation | Isolatoin | [7 empty] | C12 | 50 | 00134 | A06 | 00124 |  |  |  | Fuse | Isolation | Isolatoin | [7 empty] | C12 | 50 | 00134 | A06 | 00124 |  |  |  | Fuse | Isolation | Isolatoin | [7 empty] | C12 | 50 | 00134 | A06 | 00124 | Dual Sensing Fuses |  |  |  | Fuse | Isolation | Isolatoin
[12 empty] | C14 | 65 | 00135 | A07 | 00125 |  | Fuse Size | Amps | Co. # | Link | Link Co. # | [7 empty] | C14 | 65 | 00135 | A07 | 00125 |  | Fuse Size | Amps | Co. # | Link | Link Co. # | [7 empty] | C14 | 65 | 00135 | A07 | 00125 |  | Fuse Size | Amps | Co. # | Link | Link Co. # | [7 empty] | C14 | 65 | 00135 | A07 | 00125 | Dual Sensing Fuses |  | Fuse Size | Amps | Co. # | Link | Link Co. #
[12 empty] | C18 | 140 | 00138 | A07 | 00125 |  | C05CB | 125 | 00705 | A06 | 00124 | [7 empty] | C18 | 140 | 00138 | A07 | 00125 |  | C05CB | 125 | 00705 | A06 | 00124 | [7 empty] | C18 | 140 | 00138 | A07 | 00125 |  | C05CB | 125 | 00705 | A06 | 0124 | [7 empty] | C18 | 140 | 00138 | A07 | 00125 | Dual Sensing Fuses |  | C05CB | 125 | 00705 | A06 | 0124
[66 empty] | C16 | 100 | 00144 | A05 | 00123 | Current Sensing Fuses
[66 empty] | C17 | 140 | 00137 | A05 | 00123 | Current Sensing Fuses
[66 empty] | C05CB | 125 | 00705 | A06 | 0124 | High Amp Fuses
[11 empty] | Single Phase Bayonet Fuse Chart | [20 empty] | Dual Sensing Fuses | [10 empty] | Fuse | Fuse Manufacture | Isolation | Isolation | Isolation Link
[11 empty] | HIGH AMP | DUAL SENSING |  | * CURRENT SENSING | [19 empty] | Fuse | Fuse Manufacture | Isolation | Isolation | Isolation Link |  | Fuse Size | Type Fuse | Amps | Co. # | Part # | Link | Link Co. # | Manufacture Part #
[12 empty] | 1 Phase Transformer (Phase to Ground) Applications | [19 empty] | Fuse Size | Amps | Co. # | Part # | Link | Link Co. # | Manufacture Part # |  | C03 | Dual Sensing | 3 | 00130 | 4000358C03 | A01 | 00120 | 3001861A01M
[12 empty] | 8.3 KV | [5 empty] | 15.5 / 17.2 KV |  |  |  |  | 23 KV | [8 empty] | C03 | 3 | 00130 | 4000358C03 | A01 | 00120 | 3001861A01M |  | C05 | Dual Sensing | 8 | 00131 | 4000358C05 | A02 | 00121 | 3001861A02M
[11 empty] | Kva | 2400 | 4160 | 4800 | 7200 | 7620 | 8320 | 12000 | 12470 | 13200 | 13800 | 14400 | 19920 | 20800 | 22900 | 24940 | 23000 | 27600 | 34500 |  |  | C05 | 8 | 00131 | 4000358C05 | A02 | 00121 | 3001861A02M |  | C08 | Dual Sensing | 15 | 00132 | 4000358C08 | A03 | 00122 | 3001861A03M
[11 empty] | 5 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | C08 | 15 | 00132 | 4000358C08 | A03 | 00122 | 3001861A03M |  | C10 | Dual Sensing | 25 | 00133 | 4000358C10 | A05 | 00123 | 3001861A05M
[11 empty] | 10 | C05 | C05 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | C10 | 25 | 00133 | 4000358C10 | A05 | 00123 | 3001861A05M |  | C12 | Dual Sensing | 50 | 00134 | 4000358C12 | A06 | 00124 | 3001861A06M
[11 empty] | 15 | C08 | C05 | C05 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | C03 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | C12 | 50 | 00134 | 4000358C12 | A06 | 00124 | 3001861A06M |  | C14 | Dual Sensing | 65 | 00135 | 4000358C14 | A07 | 00125 | 3001861A07M
[11 empty] | 25 | C10 | C08 | C08 | C05 | C05 | C05 | C03 | C03 | C03 | C03 | C03 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | C14 | 65 | 00135 | 4000358C14 | A07 | 00125 | 3001861A07M |  | C18 | Dual Sensing | 140 | 00138 | 4000358C18CB | A07 | 00125 | 3001861A07M
[11 empty] | 37.5 | C12 | C10 | C08 | C08 | C08 | C08 | C05 | C05 | C05 | C05 | C05 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | C18 | 140 | 00138 | 4000358C18CB | A07 | 00125 | 3001861A07M |  | C16 | CurrentSensing | 100 | 00144 | C16 | A05 | 00123 | 3001861A05M
[11 empty] | 50 | C12 | C10 | C10 | C08 | C08 | C08 | C05 | C05 | C05 | C05 | C05 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [10 empty] | C17 | CurrentSensing | 140 | 00137 | C17 | A05 | 00123 | 3001861A05M
[11 empty] | 75 | C14 | C12 | C12 | C10 | C10 | C10 | C08 | C08 | C08 | C08 | C08 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Current Sensing Fuses | [7 empty] | C05CB | High Amp Overload | 125 | 00705 | 4038361C05CB | A06 | 00124 | 3001861A06M
[11 empty] | 100 | C14 | C12 | C12 | C10 | C10 | C10 | C08 | C08 | C08 | C08 | C08 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  |  | Fuse | Fuse Manufacture | Isolation | Isolatoin | Isolation Link
[11 empty] | 167 | C18 | C14 | C14 | C12 | C12 | C12 | C10 | C10 | C10 | C10 | C10 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | Fuse Size | Amps | Co. # | Part # | Link | Link Co. # | Manufacture Part #
[11 empty] | 250 | C05CB | C16 | C18 | C14 | C14 | C14 | C12 | C12 | C12 | C12 | C12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | C16 | 100 | 00144 | C16 | A05 | 00123 | 3001861A05M |  | Note: | Suffix "CB" at the end of the manufacturers part number indicates the fuse is an Intregal
[11 empty] | 333 | N/A | C18 | C18 | C14 | C14 | C14 | C12 | C12 | C12 | C12 | C12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | C17 | 140 | 00137 | C17 | A05 | 00123 | 3001861A05M |  |  | Element/Cartridge end plug design.
[11 empty] | 500 | N/A | C05CB | C05CB | C18 | C18 | C18 | C14 | C14 | C14 | C14 | C14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[11 empty] | ( * ) | Indicates Current Sensing Fuses | [19 empty] | High Amp Fuses | [7 empty] | Note: | Add suffix "B" to end of manufacturers part number to order individual fuse,
[34 empty] | Fuse | Fuse Manufacture | Isolation | Isolatoin | Isolation Link |  |  | add "M" to end of manufacturers part number to order by bags of 50 fuses.
[12 empty] | Dual Sensing Fuses | [5 empty] | Current Sensing Fuses | [13 empty] | Fuse Size | Amps | Co. # | Part # | Link | Link Co. # | Manufacture Part #
[14 empty] | Fuse | Isolation | Isolatoin |  |  |  | Fuse | Isolation | Isolatoin | [9 empty] | C05CB | 125 | 00705 | 4038361C05CB | A06 | A06 | 3001861A06M
[12 empty] | Fuse Size | Amps | Co. # | Link | Link Co. # |  | Fuse Size | Amps | Co. # | Link | Link Co. #
[12 empty] | C03 | 3 | 00130 | A01 | 00120 |  | C16 | 100 | 00136 | A05 | 00123
[12 empty] | C05 | 8 | 00131 | A02 | 00121
[12 empty] | C08 | 15 | 00132 | A03 | 00122
[12 empty] | C10 | 25 | 00133 | A05 | 00123 |  | High Amp Fuses
[12 empty] | C12 | 50 | 00134 | A06 | 00124 |  |  |  | Fuse | Isolation | Isolatoin
[12 empty] | C14 | 65 | 00135 | A07 | 00125 |  | Fuse Size | Amps | Co. # | Link | Link Co. #
[12 empty] | C18 | 140 | 00138 | A07 | 00125 |  | C05CB | 125 | 00705 | A06 | 0124

## _SSC (hidden)
{"IsHide":false,"HiddenInExcel":false,"SheetId":-1,"Name":"Delta Wye-Delta Delta 3 Phase","Guid":"I30VHY","Index":1,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""},"IsPrintSheet":false} | {"InputDetection":0,"RecalcMode":1,"Layout":0,"LayoutSamePagesHeightEnabled":false,"Theme":{"BgColor":"#FFFFFFFF","BgImage":"","InputBorderStyle":2,"AppliedTheme":""},"SmartphoneSettings":{"ViewportLock":true,"UseOldViewEngine":false,"EnableZoom":false,"EnableSwipe":false,"HideToolbar":false,"InheritBackgroundColor":false,"CheckboxFlavor":1,"ShowBubble":false},"Name":"","Flavor":0,"Edition":3,"CopyProtect":{"IsEnabled":false,"DomainName":""},"HideSscPoweredlogo":false,"AspnetConfig":{"BrowseUrl":"http://localhost/ssc","FileExtension":0},"NodeSecureLoginEnabled":false,"SmartphoneTheme":1,"Toolbar":{"Position":1,"IsSubmit":true,"IsPrintSheet":false,"IsPrintAll":true,"IsPrintThis":false,"IsReset":true,"IsUpdate":true},"ConfigureSubmit":{"IsShowCaptcha":false,"IsUseSscWebServer":true,"ReceiverCode":"rkooser@gmail.com","IsFreeService":false,"IsAdvanceService":false,"IsSecureEmail":false,"IsDemonstrationService":true,"AfterSuccessfulSubmit":"","AfterFailSubmit":"","AfterCancelWizard":"","IsUseOwnWebServer":false,"OwnWebServerURL":"","OwnWebServerTarget":"","SubmitTarget":0},"IgnoreBgInputCell":false,"ButtonStyle":0,"ResponsiveDesignDisabled":false,"HideLookupRange":true,"BrowserStorageEnabled":true,"RealtimeSyncEnabled":true,"GoogleAnalyticsTrackingId":"","GoogleApiKey":"","ChartSelected":3,"ChartYAxisFixed":false} | {"BrowserAndLocation":{"ConversionPath":"C:\\Users\\rkooser\\Documents\\SpreadsheetConverter","SelectedBrowsers":[]},"SpreadsheetServer":{"Username":"","Password":"","ServerUrl":"","TestUsername":"","TestPassword":""},"ConfigureSubmitDefault":{"Email":"rkooser@gmail.com","Free":false,"Advanced":false,"AdvancedSecured":false,"Demo":true},"MessageBubble":{"Close":false,"TopMsg":0},"CustomizeTheme":{"Theme":"C:\\Users\\user\\AppData\\Roaming\\SpreadsheetConverter\\V8\\SupportFiles\\themes\\bootstrap\\css\\default-ssc-theme.css"},"QrSetting":{"ShowOnConversion":true},"CongratsPage":{"LastOpenedVersion":""},"WordPressPluginSetting":{"IsPluginInstalled":false},"Preferences":{"IsAdvancedSettingModelInitialize":true,"IsCaptchaInitialize":true,"IsNodeSettingInitialize":false,"IsRequiredFieldModalInitialize":true,"IsSubmitDialogModelInitialize":true,"IsToolbarButtonModelInitialize":true,"IsWizardButtonModelInitialize":true,"ReadFromHidden":false,"AdvancedSetting":null,"NodeSetting":{"LoginText":{"LoginButtonText":"Login","PageDescription":"Restricted access only","LoginErrorMessage":"Authentication failed, please check your username and password.","PlaceholderPassword":"password","PlaceholderUsername":"username / email","UserExtraMessage":""}},"Captcha":{"Heading":"Enter the number displayed below.","Message":"This is to verify that you are a human visitor, to prevent automated form submissions.","OkButton":"OK","CancelButton":"Cancel","ErrorMessage":"Your answer is incorrect, please try again."},"RequiredField":{"ErrorMessage":"The fields with the red border are required or invalid.","OkButton":"OK","DDLDefaultRequiredText":"Please Select"},"WizardButton":{"Next":"Next","Previous":"Previous","Cancel":"Cancel","Finish":"Finish"},"ToolbarButton":{"Submit":"Submit","PrintSheet":"Print","PrintAll":"Print All","Reset":"Reset","Update":"Update","Back":"Back","PrintThis":"Print This"},"SubmitDialog":{"SubmitDialogHeading":"Submit Successful.","SubmitDialogDesc":"The form was successfully submitted.","BeforeSubmitDesc":"The form is being submitted.","OfflineHeading":"Save until online","OfflineDesc":"You are currently offline and the submit failed. Do you want to save the submit and send it later when you are online.","OfflineConfirm":"Do you want to save?","OfflineSubmitHeading":"Offline forms submit confirmation","OfflineSubmitDesc":"There are Offline form(s), which are now ready to submit in server.","OfflineSubmitConfirm":"Do you want to submit?","FailOfflineHeading":"Offline Form submit failed","FailOfflineDesc":"Unable to connect to the Internet. Please try submitting the offline forms later in internet connection.","OfflineSubmitWait":"It may take sometime to finish all submits depending on the size of offline forms and internet connection.","OfflineSubmitWaitCounter":"Left","OfflineSubmitError":"Submit error: Please try later."}},"UxPreferences":null}